## Instructions
This spreadsheet serves as a template for ASHRAE Standard 205 compliant representations corresponding to RS0002 "Unitary Cooling Air-Conditioning Equipment".
General Instructions:
Only the names and values are read out of this sheet using the SI-unit system defined in the standard. Any other columns are for user-information only.
Do not change Data Group, Data Element, or sheet names. These are used to translate the spreadsheet into simulation data.
If data group is not required, it's required elements are only required if the data group is present
RSID, RSVersion, and RSTitle should not be changed (they are set by the schema associated with this template).
Performance maps and array data groups each have separate sheets to enable an extensible number of entries in consecutive rows.
Performance map grid variables are colored in blue and must be entered in the order defined by the standard (with the rightmost column varying with the highest frequency)
The structure of the data here does not necessarily reflect the actual hierarchical data structure as defined in the standard. It has been modified for user readability, but contains all necessary data elements for simulation purposes.
This instruction sheet is informative only. It may be removed once data entry is complete.

## RS0002
Data Group | Data Element | Value | Units | Required?
ASHRAE205 |  |  |  | Yes
| RSID | RS0002 |  | Yes
| RSVersion | 0.1.0 |  | Yes
| RSTitle | Unitary Cooling Air-Conditioning Equipment |  | Yes
| ID | UID123456789 |  | Yes
| dataTimeStamp | 2019-02-07 10:10 |  | Yes
| dataVersion | A205DV-1
| description | Variable Speed Air Conditioner
| dataSource | ACSelect
notes
Description/ProductInformation
| outdoorUnitManufacturer | ColdAirInc |  | Yes
| outdoorUnitModelNumber | AC.2019.01 |  | Yes
| indoorUnitManufacturer | ColdAirInc
| indoorUnitModelNumber | AC.2019.02
| refrigerantType | R410A
| compressorType | Variable Speed Scroll
Description/RatingAHRI210240
| certifiedReferenceNumber | 456789 |  | Yes
| testStandardYear | 2017 |  | Yes
| manufacturerDataSourceVersion | 1.1.0 |  | Yes
| SEER | 22.5 | Btu/W-h | Yes
| EER | 14.5 | Btu/W-h | Yes
| capacity | 35600 | Btu/h | Yes
| ratingFanPowerPerFlow |  | W/(m3/s)
Description/RatingAHRI340360
| certifiedReferenceNumber |  |  | Yes
| testStandardYear |  |  | Yes
| manufacturerDataSourceVersion |  |  | Yes
| IEER |  | Btu/W-h | Yes
| EER |  | Btu/W-h | Yes
| capacity |  | Btu/h | Yes
| ratingFanPowerPerFlow |  | W/(m3/s)
Performance |  |  |  | Yes
| compressorControlMethod | Dynamic |  | Yes
fanRS
| fanPosition | BlowThrough |  | Yes
| nominalVolumetricAirFlowRate | 0.59 | m3/s | Yes
| cyclingDegradationCoefficient | 0.25 |  | Yes

## PerformanceMapCooling
outdoorCoilEnteringDryBulbTemperature | indoorCoilEnteringWetBulbTemperature | indoorCoilEnteringDryBulbTemperature | indoorCoilVolumetricFlowRatio | compressorSpeedRatio | ambientAbsoluteAirPressure | grossTotalCoolingCapacity | grossSensibleCoolingCapacity | grossCoolingPower
°C | °C | °C | L/s |  | Pa | W | W | W
23.9 | 15 | 24 | 179 | 1 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 15 | 24 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 248 | 1 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 15 | 24 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 264 | 2 | 101.325 | 5.8 | 5.336 | 0.73
23.9 | 15 | 24 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 267 | 1 | 101.325 | 4 | 4 | 0.36
23.9 | 15 | 24 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 378 | 2 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 15 | 24 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 389 | 2 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 15 | 24 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 24 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 179 | 1 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 15 | 27 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 248 | 1 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 15 | 27 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 264 | 2 | 101.325 | 5.8 | 5.8 | 0.73
23.9 | 15 | 27 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 267 | 1 | 101.325 | 4 | 4 | 0.36
23.9 | 15 | 27 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 378 | 2 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 15 | 27 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 389 | 2 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 15 | 27 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 27 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 179 | 1 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 15 | 29 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 248 | 1 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 15 | 29 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 264 | 2 | 101.325 | 5.8 | 5.8 | 0.73
23.9 | 15 | 29 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 267 | 1 | 101.325 | 4 | 4 | 0.36
23.9 | 15 | 29 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 378 | 2 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 15 | 29 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 389 | 2 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 15 | 29 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 15 | 29 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 179 | 1 | 101.325 | 3.5 | 2.835 | 0.4
23.9 | 17.2 | 24 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 248 | 1 | 101.325 | 3.9 | 3.549 | 0.37
23.9 | 17.2 | 24 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 264 | 2 | 101.325 | 6 | 4.5 | 0.72
23.9 | 17.2 | 24 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 267 | 1 | 101.325 | 4 | 3.76 | 0.36
23.9 | 17.2 | 24 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 378 | 2 | 101.325 | 6.5 | 5.46 | 0.68
23.9 | 17.2 | 24 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 389 | 2 | 101.325 | 6.6 | 5.61 | 0.68
23.9 | 17.2 | 24 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 24 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 179 | 1 | 101.325 | 3.5 | 3.395 | 0.4
23.9 | 17.2 | 27 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 248 | 1 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 17.2 | 27 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 264 | 2 | 101.325 | 6 | 5.28 | 0.72
23.9 | 17.2 | 27 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 267 | 1 | 101.325 | 4 | 4 | 0.36
23.9 | 17.2 | 27 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 378 | 2 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 17.2 | 27 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 389 | 2 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 17.2 | 27 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 27 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 179 | 1 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 17.2 | 29 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 248 | 1 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 17.2 | 29 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 264 | 2 | 101.325 | 6 | 6 | 0.72
23.9 | 17.2 | 29 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 267 | 1 | 101.325 | 4 | 4 | 0.36
23.9 | 17.2 | 29 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 378 | 2 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 17.2 | 29 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 389 | 2 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 17.2 | 29 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 17.2 | 29 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 179 | 1 | 101.325 | 3.8 | 2.356 | 0.38
23.9 | 19.4 | 24 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 248 | 1 | 101.325 | 4 | 2.76 | 0.35
23.9 | 19.4 | 24 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 264 | 2 | 101.325 | 6.4 | 3.776 | 0.69
23.9 | 19.4 | 24 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 267 | 1 | 101.325 | 4.1 | 2.87 | 0.35
23.9 | 19.4 | 24 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 378 | 2 | 101.325 | 6.9 | 4.416 | 0.66
23.9 | 19.4 | 24 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 389 | 2 | 101.325 | 6.9 | 4.485 | 0.65
23.9 | 19.4 | 24 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 24 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 179 | 1 | 101.325 | 3.8 | 2.964 | 0.38
23.9 | 19.4 | 27 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 248 | 1 | 101.325 | 4 | 3.52 | 0.35
23.9 | 19.4 | 27 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 264 | 2 | 101.325 | 6.4 | 4.608 | 0.69
23.9 | 19.4 | 27 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 267 | 1 | 101.325 | 4.1 | 3.731 | 0.35
23.9 | 19.4 | 27 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 378 | 2 | 101.325 | 6.9 | 5.589 | 0.66
23.9 | 19.4 | 27 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 389 | 2 | 101.325 | 6.9 | 5.658 | 0.65
23.9 | 19.4 | 27 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 27 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 179 | 1 | 101.325 | 3.8 | 3.534 | 0.38
23.9 | 19.4 | 29 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 248 | 1 | 101.325 | 4 | 4 | 0.35
23.9 | 19.4 | 29 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 264 | 2 | 101.325 | 6.4 | 5.44 | 0.69
23.9 | 19.4 | 29 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 267 | 1 | 101.325 | 4.1 | 4.1 | 0.35
23.9 | 19.4 | 29 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 378 | 2 | 101.325 | 6.9 | 6.693 | 0.66
23.9 | 19.4 | 29 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 389 | 2 | 101.325 | 6.9 | 6.762 | 0.65
23.9 | 19.4 | 29 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 19.4 | 29 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 179 | 1 | 101.325 | 4 | 1.84 | 0.35
23.9 | 21.7 | 24 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 248 | 1 | 101.325 | 4.3 | 2.107 | 0.33
23.9 | 21.7 | 24 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 264 | 2 | 101.325 | 6.7 | 3.015 | 0.67
23.9 | 21.7 | 24 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 267 | 1 | 101.325 | 4.3 | 2.15 | 0.32
23.9 | 21.7 | 24 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 378 | 2 | 101.325 | 7.3 | 3.431 | 0.63
23.9 | 21.7 | 24 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 389 | 2 | 101.325 | 7.3 | 3.504 | 0.63
23.9 | 21.7 | 24 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 24 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 179 | 1 | 101.325 | 4 | 2.44 | 0.35
23.9 | 21.7 | 27 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 248 | 1 | 101.325 | 4.3 | 2.881 | 0.33
23.9 | 21.7 | 27 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 264 | 2 | 101.325 | 6.7 | 3.886 | 0.67
23.9 | 21.7 | 27 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 267 | 1 | 101.325 | 4.3 | 2.967 | 0.32
23.9 | 21.7 | 27 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 378 | 2 | 101.325 | 7.3 | 4.599 | 0.63
23.9 | 21.7 | 27 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 389 | 2 | 101.325 | 7.3 | 4.599 | 0.63
23.9 | 21.7 | 27 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 27 | 637 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 179 | 1 | 101.325 | 4 | 3 | 0.35
23.9 | 21.7 | 29 | 179 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 179 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 248 | 1 | 101.325 | 4.3 | 3.698 | 0.33
23.9 | 21.7 | 29 | 248 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 248 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 264 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 264 | 2 | 101.325 | 6.7 | 4.69 | 0.67
23.9 | 21.7 | 29 | 264 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 267 | 1 | 101.325 | 4.3 | 3.784 | 0.32
23.9 | 21.7 | 29 | 267 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 267 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 378 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 378 | 2 | 101.325 | 7.3 | 5.767 | 0.63
23.9 | 21.7 | 29 | 378 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 389 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 389 | 2 | 101.325 | 7.3 | 5.84 | 0.63
23.9 | 21.7 | 29 | 389 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 413 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 413 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 413 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 590 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 590 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 590 | 3 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 637 | 1 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 637 | 2 | 101.325 | Null | Null | Null
23.9 | 21.7 | 29 | 637 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 179 | 1 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 15 | 24 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 248 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 15 | 24 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 264 | 2 | 101.325 | 5.6 | 5.264 | 0.89
29.4 | 15 | 24 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 267 | 1 | 101.325 | 3.7 | 3.7 | 0.47
29.4 | 15 | 24 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 378 | 2 | 101.325 | 6.3 | 6.3 | 0.86
29.4 | 15 | 24 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 389 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 15 | 24 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 413 | 3 | 101.325 | 9.3 | 8.277 | 1.79
29.4 | 15 | 24 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 590 | 3 | 101.325 | 10.5 | 10.5 | 1.75
29.4 | 15 | 24 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 24 | 637 | 3 | 101.325 | 10.8 | 10.8 | 1.73
29.4 | 15 | 27 | 179 | 1 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 15 | 27 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 248 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 15 | 27 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 264 | 2 | 101.325 | 5.6 | 5.6 | 0.89
29.4 | 15 | 27 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 267 | 1 | 101.325 | 3.7 | 3.7 | 0.47
29.4 | 15 | 27 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 378 | 2 | 101.325 | 6.3 | 6.3 | 0.86
29.4 | 15 | 27 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 389 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 15 | 27 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 413 | 3 | 101.325 | 9.3 | 9.3 | 1.79
29.4 | 15 | 27 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 590 | 3 | 101.325 | 10.5 | 10.5 | 1.75
29.4 | 15 | 27 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 27 | 637 | 3 | 101.325 | 10.8 | 10.8 | 1.73
29.4 | 15 | 29 | 179 | 1 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 15 | 29 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 248 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 15 | 29 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 264 | 2 | 101.325 | 5.6 | 5.6 | 0.89
29.4 | 15 | 29 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 267 | 1 | 101.325 | 3.7 | 3.7 | 0.47
29.4 | 15 | 29 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 378 | 2 | 101.325 | 6.3 | 6.3 | 0.86
29.4 | 15 | 29 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 389 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 15 | 29 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 413 | 3 | 101.325 | 9.3 | 9.3 | 1.79
29.4 | 15 | 29 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 590 | 3 | 101.325 | 10.5 | 10.5 | 1.75
29.4 | 15 | 29 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 15 | 29 | 637 | 3 | 101.325 | 10.8 | 10.8 | 1.73
29.4 | 17.2 | 24 | 179 | 1 | 101.325 | 3.2 | 2.72 | 0.52
29.4 | 17.2 | 24 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 248 | 1 | 101.325 | 3.6 | 3.456 | 0.48
29.4 | 17.2 | 24 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 264 | 2 | 101.325 | 5.8 | 4.408 | 0.88
29.4 | 17.2 | 24 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 267 | 1 | 101.325 | 3.6 | 3.564 | 0.48
29.4 | 17.2 | 24 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 378 | 2 | 101.325 | 6.3 | 5.418 | 0.85
29.4 | 17.2 | 24 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 389 | 2 | 101.325 | 6.3 | 5.481 | 0.85
29.4 | 17.2 | 24 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 413 | 3 | 101.325 | 9.8 | 7.154 | 1.77
29.4 | 17.2 | 24 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 590 | 3 | 101.325 | 10.7 | 8.667 | 1.74
29.4 | 17.2 | 24 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 24 | 637 | 3 | 101.325 | 10.8 | 9.072 | 1.73
29.4 | 17.2 | 27 | 179 | 1 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 17.2 | 27 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 248 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 27 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 264 | 2 | 101.325 | 5.8 | 5.22 | 0.88
29.4 | 17.2 | 27 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 267 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 27 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 378 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 27 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 389 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 27 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 413 | 3 | 101.325 | 9.8 | 8.428 | 1.77
29.4 | 17.2 | 27 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 590 | 3 | 101.325 | 10.7 | 10.379 | 1.74
29.4 | 17.2 | 27 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 27 | 637 | 3 | 101.325 | 10.8 | 10.692 | 1.73
29.4 | 17.2 | 29 | 179 | 1 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 17.2 | 29 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 248 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 29 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 264 | 2 | 101.325 | 5.8 | 5.8 | 0.88
29.4 | 17.2 | 29 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 267 | 1 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 29 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 378 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 29 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 389 | 2 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 29 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 413 | 3 | 101.325 | 9.8 | 9.604 | 1.77
29.4 | 17.2 | 29 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 590 | 3 | 101.325 | 10.7 | 10.7 | 1.74
29.4 | 17.2 | 29 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 17.2 | 29 | 637 | 3 | 101.325 | 10.8 | 10.8 | 1.73
29.4 | 19.4 | 24 | 179 | 1 | 101.325 | 3.4 | 2.21 | 0.5
29.4 | 19.4 | 24 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 248 | 1 | 101.325 | 3.6 | 2.592 | 0.47
29.4 | 19.4 | 24 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 264 | 2 | 101.325 | 6.1 | 3.66 | 0.86
29.4 | 19.4 | 24 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 267 | 1 | 101.325 | 3.7 | 2.738 | 0.47
29.4 | 19.4 | 24 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 378 | 2 | 101.325 | 6.6 | 4.356 | 0.84
29.4 | 19.4 | 24 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 389 | 2 | 101.325 | 6.6 | 4.422 | 0.83
29.4 | 19.4 | 24 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 413 | 3 | 101.325 | 10.4 | 6.032 | 1.75
29.4 | 19.4 | 24 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 590 | 3 | 101.325 | 11.3 | 7.119 | 1.71
29.4 | 19.4 | 24 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 24 | 637 | 3 | 101.325 | 11.4 | 7.41 | 1.7
29.4 | 19.4 | 27 | 179 | 1 | 101.325 | 3.4 | 2.788 | 0.5
29.4 | 19.4 | 27 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 248 | 1 | 101.325 | 3.6 | 3.348 | 0.47
29.4 | 19.4 | 27 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 264 | 2 | 101.325 | 6.1 | 4.453 | 0.86
29.4 | 19.4 | 27 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 267 | 1 | 101.325 | 3.7 | 3.552 | 0.47
29.4 | 19.4 | 27 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 378 | 2 | 101.325 | 6.6 | 5.478 | 0.84
29.4 | 19.4 | 27 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 389 | 2 | 101.325 | 6.6 | 5.544 | 0.83
29.4 | 19.4 | 27 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 413 | 3 | 101.325 | 10.4 | 7.28 | 1.75
29.4 | 19.4 | 27 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 590 | 3 | 101.325 | 11.3 | 8.927 | 1.71
29.4 | 19.4 | 27 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 27 | 637 | 3 | 101.325 | 11.4 | 9.234 | 1.7
29.4 | 19.4 | 29 | 179 | 1 | 101.325 | 3.4 | 3.332 | 0.5
29.4 | 19.4 | 29 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 248 | 1 | 101.325 | 3.6 | 3.6 | 0.47
29.4 | 19.4 | 29 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 264 | 2 | 101.325 | 6.1 | 5.307 | 0.86
29.4 | 19.4 | 29 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 267 | 1 | 101.325 | 3.7 | 3.7 | 0.47
29.4 | 19.4 | 29 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 378 | 2 | 101.325 | 6.6 | 6.534 | 0.84
29.4 | 19.4 | 29 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 389 | 2 | 101.325 | 6.6 | 6.6 | 0.83
29.4 | 19.4 | 29 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 413 | 3 | 101.325 | 10.4 | 8.528 | 1.75
29.4 | 19.4 | 29 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 590 | 3 | 101.325 | 11.3 | 10.509 | 1.71
29.4 | 19.4 | 29 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 19.4 | 29 | 637 | 3 | 101.325 | 11.4 | 10.944 | 1.7
29.4 | 21.7 | 24 | 179 | 1 | 101.325 | 3.7 | 1.739 | 0.47
29.4 | 21.7 | 24 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 248 | 1 | 101.325 | 3.9 | 1.989 | 0.45
29.4 | 21.7 | 24 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 264 | 2 | 101.325 | 6.4 | 2.944 | 0.84
29.4 | 21.7 | 24 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 267 | 1 | 101.325 | 3.9 | 1.989 | 0.45
29.4 | 21.7 | 24 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 378 | 2 | 101.325 | 7 | 3.36 | 0.81
29.4 | 21.7 | 24 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 389 | 2 | 101.325 | 7 | 3.43 | 0.81
29.4 | 21.7 | 24 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 413 | 3 | 101.325 | 11 | 4.95 | 1.72
29.4 | 21.7 | 24 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 590 | 3 | 101.325 | 11.9 | 5.712 | 1.68
29.4 | 21.7 | 24 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 24 | 637 | 3 | 101.325 | 12 | 5.88 | 1.67
29.4 | 21.7 | 27 | 179 | 1 | 101.325 | 3.7 | 2.331 | 0.47
29.4 | 21.7 | 27 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 248 | 1 | 101.325 | 3.9 | 2.769 | 0.45
29.4 | 21.7 | 27 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 264 | 2 | 101.325 | 6.4 | 3.712 | 0.84
29.4 | 21.7 | 27 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 267 | 1 | 101.325 | 3.9 | 2.847 | 0.45
29.4 | 21.7 | 27 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 378 | 2 | 101.325 | 7 | 4.55 | 0.81
29.4 | 21.7 | 27 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 389 | 2 | 101.325 | 7 | 4.62 | 0.81
29.4 | 21.7 | 27 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 413 | 3 | 101.325 | 11 | 6.27 | 1.72
29.4 | 21.7 | 27 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 590 | 3 | 101.325 | 11.9 | 7.378 | 1.68
29.4 | 21.7 | 27 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 27 | 637 | 3 | 101.325 | 12 | 7.68 | 1.67
29.4 | 21.7 | 29 | 179 | 1 | 101.325 | 3.7 | 2.923 | 0.47
29.4 | 21.7 | 29 | 179 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 179 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 248 | 1 | 101.325 | 3.9 | 3.51 | 0.45
29.4 | 21.7 | 29 | 248 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 248 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 264 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 264 | 2 | 101.325 | 6.4 | 4.544 | 0.84
29.4 | 21.7 | 29 | 264 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 267 | 1 | 101.325 | 3.9 | 3.627 | 0.45
29.4 | 21.7 | 29 | 267 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 267 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 378 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 378 | 2 | 101.325 | 7 | 5.67 | 0.81
29.4 | 21.7 | 29 | 378 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 389 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 389 | 2 | 101.325 | 7 | 5.74 | 0.81
29.4 | 21.7 | 29 | 389 | 3 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 413 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 413 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 413 | 3 | 101.325 | 11 | 7.48 | 1.72
29.4 | 21.7 | 29 | 590 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 590 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 590 | 3 | 101.325 | 11.9 | 9.044 | 1.68
29.4 | 21.7 | 29 | 637 | 1 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 637 | 2 | 101.325 | Null | Null | Null
29.4 | 21.7 | 29 | 637 | 3 | 101.325 | 12 | 9.48 | 1.67
35 | 15 | 24 | 179 | 1 | 101.325 | 3 | 3 | 0.64
35 | 15 | 24 | 179 | 2 | 101.325 | Null | Null | Null
35 | 15 | 24 | 179 | 3 | 101.325 | Null | Null | Null
35 | 15 | 24 | 248 | 1 | 101.325 | 3 | 3 | 0.62
35 | 15 | 24 | 248 | 2 | 101.325 | Null | Null | Null
35 | 15 | 24 | 248 | 3 | 101.325 | Null | Null | Null
35 | 15 | 24 | 264 | 1 | 101.325 | Null | Null | Null
35 | 15 | 24 | 264 | 2 | 101.325 | 5.4 | 5.184 | 1.07
35 | 15 | 24 | 264 | 3 | 101.325 | Null | Null | Null
35 | 15 | 24 | 267 | 1 | 101.325 | 3 | 3 | 0.61
35 | 15 | 24 | 267 | 2 | 101.325 | Null | Null | Null
35 | 15 | 24 | 267 | 3 | 101.325 | Null | Null | Null
35 | 15 | 24 | 378 | 1 | 101.325 | Null | Null | Null
35 | 15 | 24 | 378 | 2 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 24 | 378 | 3 | 101.325 | Null | Null | Null
35 | 15 | 24 | 389 | 1 | 101.325 | Null | Null | Null
35 | 15 | 24 | 389 | 2 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 24 | 389 | 3 | 101.325 | Null | Null | Null
35 | 15 | 24 | 413 | 1 | 101.325 | Null | Null | Null
35 | 15 | 24 | 413 | 2 | 101.325 | Null | Null | Null
35 | 15 | 24 | 413 | 3 | 101.325 | 9 | 8.19 | 2.08
35 | 15 | 24 | 590 | 1 | 101.325 | Null | Null | Null
35 | 15 | 24 | 590 | 2 | 101.325 | Null | Null | Null
35 | 15 | 24 | 590 | 3 | 101.325 | 10.1 | 10.1 | 2.04
35 | 15 | 24 | 637 | 1 | 101.325 | Null | Null | Null
35 | 15 | 24 | 637 | 2 | 101.325 | Null | Null | Null
35 | 15 | 24 | 637 | 3 | 101.325 | 10.4 | 10.4 | 2.02
35 | 15 | 27 | 179 | 1 | 101.325 | 3 | 3 | 0.64
35 | 15 | 27 | 179 | 2 | 101.325 | Null | Null | Null
35 | 15 | 27 | 179 | 3 | 101.325 | Null | Null | Null
35 | 15 | 27 | 248 | 1 | 101.325 | 3 | 3 | 0.62
35 | 15 | 27 | 248 | 2 | 101.325 | Null | Null | Null
35 | 15 | 27 | 248 | 3 | 101.325 | Null | Null | Null
35 | 15 | 27 | 264 | 1 | 101.325 | Null | Null | Null
35 | 15 | 27 | 264 | 2 | 101.325 | 5.4 | 5.4 | 1.07
35 | 15 | 27 | 264 | 3 | 101.325 | Null | Null | Null
35 | 15 | 27 | 267 | 1 | 101.325 | 3 | 3 | 0.61
35 | 15 | 27 | 267 | 2 | 101.325 | Null | Null | Null
35 | 15 | 27 | 267 | 3 | 101.325 | Null | Null | Null
35 | 15 | 27 | 378 | 1 | 101.325 | Null | Null | Null
35 | 15 | 27 | 378 | 2 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 27 | 378 | 3 | 101.325 | Null | Null | Null
35 | 15 | 27 | 389 | 1 | 101.325 | Null | Null | Null
35 | 15 | 27 | 389 | 2 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 27 | 389 | 3 | 101.325 | Null | Null | Null
35 | 15 | 27 | 413 | 1 | 101.325 | Null | Null | Null
35 | 15 | 27 | 413 | 2 | 101.325 | Null | Null | Null
35 | 15 | 27 | 413 | 3 | 101.325 | 9 | 9 | 2.08
35 | 15 | 27 | 590 | 1 | 101.325 | Null | Null | Null
35 | 15 | 27 | 590 | 2 | 101.325 | Null | Null | Null
35 | 15 | 27 | 590 | 3 | 101.325 | 10.1 | 10.1 | 2.04
35 | 15 | 27 | 637 | 1 | 101.325 | Null | Null | Null
35 | 15 | 27 | 637 | 2 | 101.325 | Null | Null | Null
35 | 15 | 27 | 637 | 3 | 101.325 | 10.4 | 10.4 | 2.02
35 | 15 | 29 | 179 | 1 | 101.325 | 3 | 3 | 0.64
35 | 15 | 29 | 179 | 2 | 101.325 | Null | Null | Null
35 | 15 | 29 | 179 | 3 | 101.325 | Null | Null | Null
35 | 15 | 29 | 248 | 1 | 101.325 | 3 | 3 | 0.62
35 | 15 | 29 | 248 | 2 | 101.325 | Null | Null | Null
35 | 15 | 29 | 248 | 3 | 101.325 | Null | Null | Null
35 | 15 | 29 | 264 | 1 | 101.325 | Null | Null | Null
35 | 15 | 29 | 264 | 2 | 101.325 | 5.4 | 5.4 | 1.07
35 | 15 | 29 | 264 | 3 | 101.325 | Null | Null | Null
35 | 15 | 29 | 267 | 1 | 101.325 | 3 | 3 | 0.61
35 | 15 | 29 | 267 | 2 | 101.325 | Null | Null | Null
35 | 15 | 29 | 267 | 3 | 101.325 | Null | Null | Null
35 | 15 | 29 | 378 | 1 | 101.325 | Null | Null | Null
35 | 15 | 29 | 378 | 2 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 29 | 378 | 3 | 101.325 | Null | Null | Null
35 | 15 | 29 | 389 | 1 | 101.325 | Null | Null | Null
35 | 15 | 29 | 389 | 2 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 29 | 389 | 3 | 101.325 | Null | Null | Null
35 | 15 | 29 | 413 | 1 | 101.325 | Null | Null | Null
35 | 15 | 29 | 413 | 2 | 101.325 | Null | Null | Null
35 | 15 | 29 | 413 | 3 | 101.325 | 9 | 9 | 2.08
35 | 15 | 29 | 590 | 1 | 101.325 | Null | Null | Null
35 | 15 | 29 | 590 | 2 | 101.325 | Null | Null | Null
35 | 15 | 29 | 590 | 3 | 101.325 | 10.1 | 10.1 | 2.04
35 | 15 | 29 | 637 | 1 | 101.325 | Null | Null | Null
35 | 15 | 29 | 637 | 2 | 101.325 | Null | Null | Null
35 | 15 | 29 | 637 | 3 | 101.325 | 10.4 | 10.4 | 2.02
35 | 17.2 | 24 | 179 | 1 | 101.325 | 3 | 2.67 | 0.65
35 | 17.2 | 24 | 179 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 179 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 248 | 1 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 24 | 248 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 248 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 264 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 264 | 2 | 101.325 | 5.5 | 4.29 | 1.06
35 | 17.2 | 24 | 264 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 267 | 1 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 24 | 267 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 267 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 378 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 378 | 2 | 101.325 | 5.5 | 4.84 | 1.04
35 | 17.2 | 24 | 378 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 389 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 389 | 2 | 101.325 | 5.5 | 4.895 | 1.04
35 | 17.2 | 24 | 389 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 413 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 413 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 413 | 3 | 101.325 | 9.4 | 6.956 | 2.06
35 | 17.2 | 24 | 590 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 590 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 590 | 3 | 101.325 | 10.1 | 8.383 | 2.03
35 | 17.2 | 24 | 637 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 637 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 24 | 637 | 3 | 101.325 | 10.4 | 8.944 | 2.02
35 | 17.2 | 27 | 179 | 1 | 101.325 | 3 | 3 | 0.65
35 | 17.2 | 27 | 179 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 179 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 248 | 1 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 27 | 248 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 248 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 264 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 264 | 2 | 101.325 | 5.5 | 5.115 | 1.06
35 | 17.2 | 27 | 264 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 267 | 1 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 27 | 267 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 267 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 378 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 378 | 2 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 27 | 378 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 389 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 389 | 2 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 27 | 389 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 413 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 413 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 413 | 3 | 101.325 | 9.4 | 8.272 | 2.06
35 | 17.2 | 27 | 590 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 590 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 590 | 3 | 101.325 | 10.1 | 9.999 | 2.03
35 | 17.2 | 27 | 637 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 637 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 27 | 637 | 3 | 101.325 | 10.4 | 10.4 | 2.02
35 | 17.2 | 29 | 179 | 1 | 101.325 | 3 | 3 | 0.65
35 | 17.2 | 29 | 179 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 179 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 248 | 1 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 29 | 248 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 248 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 264 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 264 | 2 | 101.325 | 5.5 | 5.5 | 1.06
35 | 17.2 | 29 | 264 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 267 | 1 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 29 | 267 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 267 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 378 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 378 | 2 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 29 | 378 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 389 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 389 | 2 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 29 | 389 | 3 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 413 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 413 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 413 | 3 | 101.325 | 9.4 | 9.4 | 2.06
35 | 17.2 | 29 | 590 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 590 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 590 | 3 | 101.325 | 10.1 | 10.1 | 2.03
35 | 17.2 | 29 | 637 | 1 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 637 | 2 | 101.325 | Null | Null | Null
35 | 17.2 | 29 | 637 | 3 | 101.325 | 10.4 | 10.4 | 2.02
35 | 19.4 | 24 | 179 | 1 | 101.325 | 3.1 | 2.077 | 0.63
35 | 19.4 | 24 | 179 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 179 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 248 | 1 | 101.325 | 3.1 | 2.325 | 0.61
35 | 19.4 | 24 | 248 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 248 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 264 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 264 | 2 | 101.325 | 5.8 | 3.538 | 1.05
35 | 19.4 | 24 | 264 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 267 | 1 | 101.325 | 3.1 | 2.418 | 0.61
35 | 19.4 | 24 | 267 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 267 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 378 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 378 | 2 | 101.325 | 5.8 | 3.886 | 1.03
35 | 19.4 | 24 | 378 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 389 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 389 | 2 | 101.325 | 5.8 | 3.944 | 1.03
35 | 19.4 | 24 | 389 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 413 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 413 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 413 | 3 | 101.325 | 10 | 5.9 | 2.03
35 | 19.4 | 24 | 590 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 590 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 590 | 3 | 101.325 | 10.7 | 6.955 | 2.01
35 | 19.4 | 24 | 637 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 637 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 24 | 637 | 3 | 101.325 | 10.9 | 7.194 | 1.99
35 | 19.4 | 27 | 179 | 1 | 101.325 | 3.1 | 2.666 | 0.63
35 | 19.4 | 27 | 179 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 179 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 248 | 1 | 101.325 | 3.1 | 3.038 | 0.61
35 | 19.4 | 27 | 248 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 248 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 264 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 264 | 2 | 101.325 | 5.8 | 4.35 | 1.05
35 | 19.4 | 27 | 264 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.61
35 | 19.4 | 27 | 267 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 267 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 378 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 378 | 2 | 101.325 | 5.8 | 4.988 | 1.03
35 | 19.4 | 27 | 378 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 389 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 389 | 2 | 101.325 | 5.8 | 5.046 | 1.03
35 | 19.4 | 27 | 389 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 413 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 413 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 413 | 3 | 101.325 | 10 | 7.2 | 2.03
35 | 19.4 | 27 | 590 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 590 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 590 | 3 | 101.325 | 10.7 | 8.667 | 2.01
35 | 19.4 | 27 | 637 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 637 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 27 | 637 | 3 | 101.325 | 10.9 | 9.047 | 1.99
35 | 19.4 | 29 | 179 | 1 | 101.325 | 3.1 | 3.1 | 0.63
35 | 19.4 | 29 | 179 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 179 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.61
35 | 19.4 | 29 | 248 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 248 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 264 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 264 | 2 | 101.325 | 5.8 | 5.162 | 1.05
35 | 19.4 | 29 | 264 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.61
35 | 19.4 | 29 | 267 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 267 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 378 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 378 | 2 | 101.325 | 5.8 | 5.8 | 1.03
35 | 19.4 | 29 | 378 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 389 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 389 | 2 | 101.325 | 5.8 | 5.8 | 1.03
35 | 19.4 | 29 | 389 | 3 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 413 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 413 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 413 | 3 | 101.325 | 10 | 8.4 | 2.03
35 | 19.4 | 29 | 590 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 590 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 590 | 3 | 101.325 | 10.7 | 10.272 | 2.01
35 | 19.4 | 29 | 637 | 1 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 637 | 2 | 101.325 | Null | Null | Null
35 | 19.4 | 29 | 637 | 3 | 101.325 | 10.9 | 10.791 | 1.99
35 | 21.7 | 24 | 179 | 1 | 101.325 | 3.3 | 1.584 | 0.61
35 | 21.7 | 24 | 179 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 179 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 248 | 1 | 101.325 | 3.3 | 1.716 | 0.59
35 | 21.7 | 24 | 248 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 248 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 264 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 264 | 2 | 101.325 | 6.2 | 2.852 | 1.03
35 | 21.7 | 24 | 264 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 267 | 1 | 101.325 | 3.3 | 1.749 | 0.59
35 | 21.7 | 24 | 267 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 267 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 378 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 378 | 2 | 101.325 | 6.2 | 3.038 | 1.01
35 | 21.7 | 24 | 378 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 389 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 389 | 2 | 101.325 | 6.2 | 3.038 | 1.01
35 | 21.7 | 24 | 389 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 413 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 413 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 413 | 3 | 101.325 | 10.5 | 4.83 | 2.01
35 | 21.7 | 24 | 590 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 590 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 590 | 3 | 101.325 | 11.3 | 5.424 | 1.97
35 | 21.7 | 24 | 637 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 637 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 24 | 637 | 3 | 101.325 | 11.6 | 5.684 | 1.97
35 | 21.7 | 27 | 179 | 1 | 101.325 | 3.3 | 2.178 | 0.61
35 | 21.7 | 27 | 179 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 179 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 248 | 1 | 101.325 | 3.3 | 2.442 | 0.59
35 | 21.7 | 27 | 248 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 248 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 264 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 264 | 2 | 101.325 | 6.2 | 3.658 | 1.03
35 | 21.7 | 27 | 264 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 267 | 1 | 101.325 | 3.3 | 2.541 | 0.59
35 | 21.7 | 27 | 267 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 267 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 378 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 378 | 2 | 101.325 | 6.2 | 4.092 | 1.01
35 | 21.7 | 27 | 378 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 389 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 389 | 2 | 101.325 | 6.2 | 4.154 | 1.01
35 | 21.7 | 27 | 389 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 413 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 413 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 413 | 3 | 101.325 | 10.5 | 5.985 | 2.01
35 | 21.7 | 27 | 590 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 590 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 590 | 3 | 101.325 | 11.3 | 7.119 | 1.97
35 | 21.7 | 27 | 637 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 637 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 27 | 637 | 3 | 101.325 | 11.6 | 7.54 | 1.97
35 | 21.7 | 29 | 179 | 1 | 101.325 | 3.3 | 2.706 | 0.61
35 | 21.7 | 29 | 179 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 179 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 248 | 1 | 101.325 | 3.3 | 3.135 | 0.59
35 | 21.7 | 29 | 248 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 248 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 264 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 264 | 2 | 101.325 | 6.2 | 4.464 | 1.03
35 | 21.7 | 29 | 264 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 267 | 1 | 101.325 | 3.3 | 3.267 | 0.59
35 | 21.7 | 29 | 267 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 267 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 378 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 378 | 2 | 101.325 | 6.2 | 5.146 | 1.01
35 | 21.7 | 29 | 378 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 389 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 389 | 2 | 101.325 | 6.2 | 5.208 | 1.01
35 | 21.7 | 29 | 389 | 3 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 413 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 413 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 413 | 3 | 101.325 | 10.5 | 7.245 | 2.01
35 | 21.7 | 29 | 590 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 590 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 590 | 3 | 101.325 | 11.3 | 8.814 | 1.97
35 | 21.7 | 29 | 637 | 1 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 637 | 2 | 101.325 | Null | Null | Null
35 | 21.7 | 29 | 637 | 3 | 101.325 | 11.6 | 9.396 | 1.97
40.6 | 15 | 24 | 179 | 1 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 15 | 24 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 24 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 264 | 2 | 101.325 | 5.1 | 5.049 | 1.27
40.6 | 15 | 24 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 24 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 378 | 2 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 15 | 24 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 389 | 2 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 15 | 24 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 413 | 3 | 101.325 | 8.6 | 7.998 | 2.38
40.6 | 15 | 24 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 590 | 3 | 101.325 | 8.6 | 8.6 | 2.34
40.6 | 15 | 24 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 24 | 637 | 3 | 101.325 | 8.6 | 8.6 | 2.33
40.6 | 15 | 27 | 179 | 1 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 15 | 27 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 27 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 264 | 2 | 101.325 | 5.1 | 5.1 | 1.27
40.6 | 15 | 27 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 27 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 378 | 2 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 15 | 27 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 389 | 2 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 15 | 27 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 413 | 3 | 101.325 | 8.6 | 8.6 | 2.38
40.6 | 15 | 27 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 590 | 3 | 101.325 | 8.6 | 8.6 | 2.34
40.6 | 15 | 27 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 27 | 637 | 3 | 101.325 | 8.6 | 8.6 | 2.33
40.6 | 15 | 29 | 179 | 1 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 15 | 29 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 29 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 264 | 2 | 101.325 | 5.1 | 5.1 | 1.27
40.6 | 15 | 29 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 29 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 378 | 2 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 15 | 29 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 389 | 2 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 15 | 29 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 413 | 3 | 101.325 | 8.6 | 8.6 | 2.38
40.6 | 15 | 29 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 590 | 3 | 101.325 | 8.6 | 8.6 | 2.34
40.6 | 15 | 29 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 15 | 29 | 637 | 3 | 101.325 | 8.6 | 8.6 | 2.33
40.6 | 17.2 | 24 | 179 | 1 | 101.325 | 2.8 | 2.604 | 0.79
40.6 | 17.2 | 24 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 17.2 | 24 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 264 | 2 | 101.325 | 5.2 | 4.16 | 1.26
40.6 | 17.2 | 24 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 17.2 | 24 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 378 | 2 | 101.325 | 5.7 | 5.187 | 1.24
40.6 | 17.2 | 24 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 389 | 2 | 101.325 | 5.8 | 5.336 | 1.24
40.6 | 17.2 | 24 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 413 | 3 | 101.325 | 8.9 | 6.764 | 2.37
40.6 | 17.2 | 24 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 590 | 3 | 101.325 | 8.9 | 7.565 | 2.34
40.6 | 17.2 | 24 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 24 | 637 | 3 | 101.325 | 8.9 | 7.832 | 2.33
40.6 | 17.2 | 27 | 179 | 1 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 17.2 | 27 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 17.2 | 27 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 264 | 2 | 101.325 | 5.2 | 4.94 | 1.26
40.6 | 17.2 | 27 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 17.2 | 27 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 378 | 2 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 17.2 | 27 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 389 | 2 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 17.2 | 27 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 413 | 3 | 101.325 | 8.9 | 8.01 | 2.37
40.6 | 17.2 | 27 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 590 | 3 | 101.325 | 8.9 | 8.9 | 2.34
40.6 | 17.2 | 27 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 27 | 637 | 3 | 101.325 | 8.9 | 8.9 | 2.33
40.6 | 17.2 | 29 | 179 | 1 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 17.2 | 29 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 17.2 | 29 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 264 | 2 | 101.325 | 5.2 | 5.2 | 1.26
40.6 | 17.2 | 29 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 17.2 | 29 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 378 | 2 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 17.2 | 29 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 389 | 2 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 17.2 | 29 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 413 | 3 | 101.325 | 8.9 | 8.9 | 2.37
40.6 | 17.2 | 29 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 590 | 3 | 101.325 | 8.9 | 8.9 | 2.34
40.6 | 17.2 | 29 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 17.2 | 29 | 637 | 3 | 101.325 | 8.9 | 8.9 | 2.33
40.6 | 19.4 | 24 | 179 | 1 | 101.325 | 2.9 | 2.03 | 0.78
40.6 | 19.4 | 24 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 248 | 1 | 101.325 | 3.1 | 2.449 | 0.76
40.6 | 19.4 | 24 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 264 | 2 | 101.325 | 5.5 | 3.41 | 1.25
40.6 | 19.4 | 24 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 267 | 1 | 101.325 | 3.1 | 2.511 | 0.75
40.6 | 19.4 | 24 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 378 | 2 | 101.325 | 5.9 | 4.071 | 1.24
40.6 | 19.4 | 24 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 389 | 2 | 101.325 | 5.9 | 4.071 | 1.24
40.6 | 19.4 | 24 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 413 | 3 | 101.325 | 9.5 | 5.7 | 2.35
40.6 | 19.4 | 24 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 590 | 3 | 101.325 | 9.5 | 6.27 | 2.31
40.6 | 19.4 | 24 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 24 | 637 | 3 | 101.325 | 9.5 | 6.46 | 2.31
40.6 | 19.4 | 27 | 179 | 1 | 101.325 | 2.9 | 2.61 | 0.78
40.6 | 19.4 | 27 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 19.4 | 27 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 264 | 2 | 101.325 | 5.5 | 4.235 | 1.25
40.6 | 19.4 | 27 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 19.4 | 27 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 378 | 2 | 101.325 | 5.9 | 5.192 | 1.24
40.6 | 19.4 | 27 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 389 | 2 | 101.325 | 5.9 | 5.31 | 1.24
40.6 | 19.4 | 27 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 413 | 3 | 101.325 | 9.5 | 6.935 | 2.35
40.6 | 19.4 | 27 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 590 | 3 | 101.325 | 9.5 | 7.885 | 2.31
40.6 | 19.4 | 27 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 27 | 637 | 3 | 101.325 | 9.5 | 8.17 | 2.31
40.6 | 19.4 | 29 | 179 | 1 | 101.325 | 2.9 | 2.9 | 0.78
40.6 | 19.4 | 29 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 248 | 1 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 19.4 | 29 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 264 | 2 | 101.325 | 5.5 | 5.06 | 1.25
40.6 | 19.4 | 29 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 267 | 1 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 19.4 | 29 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 378 | 2 | 101.325 | 5.9 | 5.9 | 1.24
40.6 | 19.4 | 29 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 389 | 2 | 101.325 | 5.9 | 5.9 | 1.24
40.6 | 19.4 | 29 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 413 | 3 | 101.325 | 9.5 | 8.17 | 2.35
40.6 | 19.4 | 29 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 590 | 3 | 101.325 | 9.5 | 9.31 | 2.31
40.6 | 19.4 | 29 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 19.4 | 29 | 637 | 3 | 101.325 | 9.5 | 9.5 | 2.31
40.6 | 21.7 | 24 | 179 | 1 | 101.325 | 3.1 | 1.519 | 0.76
40.6 | 21.7 | 24 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 248 | 1 | 101.325 | 3.3 | 1.782 | 0.74
40.6 | 21.7 | 24 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 264 | 2 | 101.325 | 5.9 | 2.714 | 1.24
40.6 | 21.7 | 24 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 267 | 1 | 101.325 | 3.3 | 1.815 | 0.74
40.6 | 21.7 | 24 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 378 | 2 | 101.325 | 6.3 | 3.087 | 1.22
40.6 | 21.7 | 24 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 389 | 2 | 101.325 | 6.3 | 3.15 | 1.22
40.6 | 21.7 | 24 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 413 | 3 | 101.325 | 10 | 4.6 | 2.32
40.6 | 21.7 | 24 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 590 | 3 | 101.325 | 10 | 4.9 | 2.29
40.6 | 21.7 | 24 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 24 | 637 | 3 | 101.325 | 10 | 5 | 2.27
40.6 | 21.7 | 27 | 179 | 1 | 101.325 | 3.1 | 2.108 | 0.76
40.6 | 21.7 | 27 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 248 | 1 | 101.325 | 3.3 | 2.574 | 0.74
40.6 | 21.7 | 27 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 264 | 2 | 101.325 | 5.9 | 3.599 | 1.24
40.6 | 21.7 | 27 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 267 | 1 | 101.325 | 3.3 | 2.64 | 0.74
40.6 | 21.7 | 27 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 378 | 2 | 101.325 | 6.3 | 4.284 | 1.22
40.6 | 21.7 | 27 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 389 | 2 | 101.325 | 6.3 | 4.347 | 1.22
40.6 | 21.7 | 27 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 413 | 3 | 101.325 | 10 | 5.8 | 2.32
40.6 | 21.7 | 27 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 590 | 3 | 101.325 | 10 | 6.4 | 2.29
40.6 | 21.7 | 27 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 27 | 637 | 3 | 101.325 | 10 | 6.7 | 2.27
40.6 | 21.7 | 29 | 179 | 1 | 101.325 | 3.1 | 2.697 | 0.76
40.6 | 21.7 | 29 | 179 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 179 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 248 | 1 | 101.325 | 3.3 | 3.3 | 0.74
40.6 | 21.7 | 29 | 248 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 248 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 264 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 264 | 2 | 101.325 | 5.9 | 4.425 | 1.24
40.6 | 21.7 | 29 | 264 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 267 | 1 | 101.325 | 3.3 | 3.3 | 0.74
40.6 | 21.7 | 29 | 267 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 267 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 378 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 378 | 2 | 101.325 | 6.3 | 5.418 | 1.22
40.6 | 21.7 | 29 | 378 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 389 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 389 | 2 | 101.325 | 6.3 | 5.481 | 1.22
40.6 | 21.7 | 29 | 389 | 3 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 413 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 413 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 413 | 3 | 101.325 | 10 | 7 | 2.32
40.6 | 21.7 | 29 | 590 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 590 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 590 | 3 | 101.325 | 10 | 8 | 2.29
40.6 | 21.7 | 29 | 637 | 1 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 637 | 2 | 101.325 | Null | Null | Null
40.6 | 21.7 | 29 | 637 | 3 | 101.325 | 10 | 8.3 | 2.27
46.1 | 15 | 24 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 413 | 3 | 101.325 | 8.2 | 7.872 | 2.72
46.1 | 15 | 24 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 590 | 3 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 15 | 24 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 24 | 637 | 3 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 15 | 27 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 413 | 3 | 101.325 | 8.2 | 8.2 | 2.72
46.1 | 15 | 27 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 590 | 3 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 15 | 27 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 27 | 637 | 3 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 15 | 29 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 413 | 3 | 101.325 | 8.2 | 8.2 | 2.72
46.1 | 15 | 29 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 590 | 3 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 15 | 29 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 15 | 29 | 637 | 3 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 17.2 | 24 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 413 | 3 | 101.325 | 8.4 | 6.468 | 2.71
46.1 | 17.2 | 24 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 590 | 3 | 101.325 | 9.2 | 8.004 | 2.67
46.1 | 17.2 | 24 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 24 | 637 | 3 | 101.325 | 9.4 | 8.554 | 2.66
46.1 | 17.2 | 27 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 413 | 3 | 101.325 | 8.4 | 7.728 | 2.71
46.1 | 17.2 | 27 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 590 | 3 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 17.2 | 27 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 27 | 637 | 3 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 17.2 | 29 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 413 | 3 | 101.325 | 8.4 | 8.4 | 2.71
46.1 | 17.2 | 29 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 590 | 3 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 17.2 | 29 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 17.2 | 29 | 637 | 3 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 19.4 | 24 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 413 | 3 | 101.325 | 9 | 5.49 | 2.68
46.1 | 19.4 | 24 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 590 | 3 | 101.325 | 9.7 | 6.499 | 2.65
46.1 | 19.4 | 24 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 24 | 637 | 3 | 101.325 | 9.8 | 6.762 | 2.64
46.1 | 19.4 | 27 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 413 | 3 | 101.325 | 9 | 6.75 | 2.68
46.1 | 19.4 | 27 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 590 | 3 | 101.325 | 9.7 | 8.245 | 2.65
46.1 | 19.4 | 27 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 27 | 637 | 3 | 101.325 | 9.8 | 8.624 | 2.64
46.1 | 19.4 | 29 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 413 | 3 | 101.325 | 9 | 8.01 | 2.68
46.1 | 19.4 | 29 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 590 | 3 | 101.325 | 9.7 | 9.7 | 2.65
46.1 | 19.4 | 29 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 19.4 | 29 | 637 | 3 | 101.325 | 9.8 | 9.8 | 2.64
46.1 | 21.7 | 24 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 413 | 3 | 101.325 | 9.5 | 4.37 | 2.66
46.1 | 21.7 | 24 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 590 | 3 | 101.325 | 10.2 | 4.998 | 2.62
46.1 | 21.7 | 24 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 24 | 637 | 3 | 101.325 | 10.4 | 5.304 | 2.61
46.1 | 21.7 | 27 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 413 | 3 | 101.325 | 9.5 | 5.605 | 2.66
46.1 | 21.7 | 27 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 590 | 3 | 101.325 | 10.2 | 6.732 | 2.62
46.1 | 21.7 | 27 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 27 | 637 | 3 | 101.325 | 10.4 | 7.072 | 2.61
46.1 | 21.7 | 29 | 179 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 179 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 179 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 248 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 248 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 248 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 264 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 264 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 264 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 267 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 267 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 267 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 378 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 378 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 378 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 389 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 389 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 389 | 3 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 413 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 413 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 413 | 3 | 101.325 | 9.5 | 6.84 | 2.66
46.1 | 21.7 | 29 | 590 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 590 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 590 | 3 | 101.325 | 10.2 | 8.364 | 2.62
46.1 | 21.7 | 29 | 637 | 1 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 637 | 2 | 101.325 | Null | Null | Null
46.1 | 21.7 | 29 | 637 | 3 | 101.325 | 10.4 | 8.944 | 2.61

## PerformanceMapStandby
outdoorCoilEnvironmentalDryBulbTemperature | grossPower
°C | W
37.78 | 0
10.5 | 0
10 | 40
-17.78 | 40